## Slide 1
David Attié
JLC13, Saclay
Two-Phase CO2 cooling
Notes: I’m here to present a TPC review

## Slide 2: Overview
Introduction: why CO2 cooling?
‘2-Phase Accumulator Controlled Loop’ CO2 circulation method
Portable cooling system: Traci
Application to a Large Prototype TPC
Conclusions

## Slide 3: Comparison of refrigerants vs. CO2
Higher slope of the vapor pressure curve means that DP in the system is smaller
Low ratio of liquid and gas densities resulting in a more homogenous two-phase flow (Pettersen 2002)
T (°C)
T (°C)
Equilibrium vapor pressure
Ratio of liquid and vapor densities
CO2
CO2

## Slide 4: Why CO2 cooling?
Evaporative CO2 cooling for HEP detectors: CO2 allows small tubing
  low radiation length X0
  compact detector
allows high
pressure drop
allows low flow
allows very
small tubing
Low pressure drop
Low pressure drop
Large latent heat
& Low viscosity
& High Pressure
(Pa*s)
Better
CO2
C3F8
1e-4
2e-4
3e-4
4e-4
5e-4
-40
-20
0
20
(KJ/kg)
Better
C3F8
CO2
100
200
300
0
-40
-20
0
20
Temperature (°C)
Temperature (°C)
bart@nikhef.nl

## Slide 5: Cooling tube
Liquid
2-phase
Gas
Pressure (bar)
Temperature (°C)
Target flow condition
Dry-out zone
Sub cooled liquid
Sub cooled liquid
Super heated vapor
bart@nikhef.nl
Liquid super heating
Low DT
Increasing DT
(Dry-out)
Fluid Temperature
Tube Temperature
Enthalpy (J/K)
-30
0
30
60
90

## Slide 6: How to evaporate liquid CO2 in your detector?
Pressure
Pressure
Enthalpy
Enthalpy
Liquid
Gas
2-phase
Liquid
Gas
2-phase
Refrigeration method: Vapor compression system
(Atlas)
2PACL method: Pumped liquid system,
(Atlas) cooled externally
bart@nikhef.nl
Compressor
Compressor
Chiller
Liquid circulation
Warm transfert
Cooling plan
Cooling plan
Detector
Detector
Cold transfert
Pump
Heater
B.p. regulator

## Slide 7: 2-Phase Accumulator Controlled Loop
Pressure
1
5
2
6
7
Liquid
Enthalpy
Gas
Isothermal line
2-phase
(Evaporation)
Pump
Pressure control
using accumulator
Change set-point
Detector: follows saturation line
Cooling
Lower the pressure
3
2
7
6
4&5
1
bart@nikhef.nl
3
4

## Slide 8: 2-Phase Accumulator Controlled Loop
Pressure
1
5
2
6
7
Liquid
Enthalpy
Gas
Isothermal line
2-phase
(Evaporation)
Pump
Cooling
Lower the pressure
7
3
2
6
4&5
1
bart@nikhef.nl
Detector: follows saturation line
3
4

## Slide 9: 2-Phase Accumulator Controlled Loop
Pressure
1
5
2
6
7
Liquid
Enthalpy
Gas
Isothermal line
2-phase
(Evaporation)
Pump
7
3
2
6
Heating
Increase pressure
of saturation
bart@nikhef.nl
1
4&5
Detector: follows saturation line
3
4

## Slide 10: 2-Phase Accumulator Controlled Loop
Pressure
1
5
2
6
7
Liquid
Enthalpy
Gas
Isothermal line
2-phase
(Evaporation)
Pump
Increasing pressure
3
2
7
6
4&5
1
Heating
Switching on detector
Heat
bart@nikhef.nl
Detector: follows saturation line
3
4

## Slide 11: 2-Phase Accumulator Controlled Loop
Cooling
Pressure
1
5
2
6
7
Liquid
Enthalpy
Gas
Isothermal line
2-phase
(Evaporation)
Pump
Heat
bart@nikhef.nl
Detector: follows saturation line
3
2
7
6
4&5
1
Powering detector
3
4

## Slide 12: 2-Phase Accumulator Controlled Loop
Pressure
1
5
2
6
7
Liquid
Enthalpy
Gas
Isothermal line
2-phase
(Evaporation)
Pump
3
2
7
6
4&5
1
Heating
Unpower detector
bart@nikhef.nl
Detector: follows saturation line
Detector is off
3
4

## Slide 13: Traci Project
Development of a portable CO2 laboratory cooling unit called Traci
  TRACI=Transportable Refrigeration Apparatus for CO2 Investigation.
Development in AIDA framework together with interested partners.
  Nikhef & CERN lead development with engineering support of the Cracow University of Technology.
  Co-funding from clients
Designed for applications like:
  Test beam telescope (AIDA)
  Micro channel development (LHCb)
  Pixel development (CMS)
  Detector thermal/mechanical support structure development (Atlas IBL, ILCTPC)
  Detector commissioning (Atlas IBL)
Focus on simplicity for easy production in series
bart@nikhef.nl

## Slide 14: Traci performance
Stable cooling over a large temperature range
bart@nikhef.nl

## Slide 15: Large Prototype Micromegas TPC for ILC
5 GeV electron beam
12 000 channels in 7 modules
24 rows
72
columns
Large Prototype (LP) TPC in DESY
Endplate + 7 Micromegas modules in 1T magnet

## Slide 16: Micromegas Module of the LP-TPC
Micromegas
Air cooling
FEM
FEC

## Slide 17: Air Cooling for the Micromegas Module
No cooling
Nitrogen cooling
Picture taken from IR camera

## Slide 18: 2P-CO2 Cooling for ILC-TPC Micromegas LP
Calculation for a
single module cooling
Internal =0.876 mm
Calculation for
7 modules cooling

## Slide 19: 7 modules in serial
A serial configuration needs a diameter of 1.5 to 2mm depending on the allowed temperature gradient.
Internal =1.5 mm
Internal = 2.0 mm

## Slide 20: Conclusions
Two operating CO2 systems in HEP experiments:
  AMS-TTCS (Tracker Thermal Control System)
  LHCb-VTCS (VELO Thermal Control System)
CO2 cooling is a suitable solution for future HEP detectors (ex: ILC)
  cheap and « natural » element
  high heat transfert with low X0
2PACL technology is interesting as a system principle:
  High stability
  Easy to operate
First test with the Micromegas detector in a Large Prototype will be done
in 2014 (February)